August 8, 2018

Lickdale, PA

The Union Township Board of Supervisors held a scheduled sewer meeting on August 8, 2018.  The meeting was held at the Municipal Building, 3111 SR 72, Jonestown, PA.

`

Chairman Firestone called the meeting to order at 6:30 PM.

Present:		Dennis Firestone, Chairman

Kerry McCrary, Vice Chairman

Gary Longenecker, Secretary

Paul Bametzreider, Township Solicitor

Scott Rights, Sewer Engineer

Brent McFeaters, Township Manager

Elizabeth Krause, Zoning Officer (absent)

Jim Darkes, Operator

Six (6) Citizens

PUBLIC COMMENTS

APPROVE THE MINUTES

Chairman Firestone presented the minutes from the July meeting for approval.  Kerry McCrary made a motion seconded by Gary Longenecker to approve the July meeting minutes.   All approved.

APPROVE THE FINANCIAL REPORT

Gary Longenecker made a motion seconded by Gary Kerry McCrary to approve the Financial Report.  All approved.

OPERATOR’S REPORT – Jim Darkes

- Recent storm flow update - Jim Darkes said there were a number of adjustments made at the plant including putting the second clarifier online due to the heavy rain.

- Platform for composite sampler – Mr. Darkes said the area where the composite sampler is located is prone to flooding and if the sampler tips over and gets covered in water, it will probably get ruined.  He noted that the cost to replace it would be around $7,000.00. He explained that they would like to build a concrete pad with some decking on a platform, so it doesn’t get ruined, and he said the NLCA will do the work.  Dennis Firestone made a motion seconded by Kerry McCrary to authorize the NLCA to take care of installing the concrete pad, the platform and any other work required in to protect the composite sampler from flooding.  All approved.

- Pump Station 2 Generator Update – Mr. Darkes said he just got an email from Penn Power stating that the delivery of the generator was slightly delayed, but it should be shipped next week.  He said it will be early September till it’s online.

- Utility Water Line in Screen Room – Jim Darkes stated that when the celluloid valves on the utility water line opens and closes, it’s creating pressures of about 130 to 140 BSI   noting that the screen, the filter and the piping in that room are only rated for approximately 110 BSI.  He said he would like to get an estimate to switch over to a different type of filter housing that could withstand the pressure to avoid any additional flooding that might occur down in the lower level.  He said he will try to get some details prior to next meeting.

- The chemical line was clogged but it is now opened and was tested today and can be placed on line. A discussion was held about upgrades to the chemical-lead-distribution system.

- USG will be on site Monday or Tuesday of next week to do the line televising.

- There are a few programming issues regarding putting Train #2 online.  The return pump is looking at the wrong flow meter and nothing can be done about it.    Mr. Darkes noted that they were hoping that the programming would be able to be done remotely, but they will now have to get a proposal for internal programming to have the problem corrected.  He also explained that when Train #2 does go online, Kruger will require themselves to be on site because the automation was not previously tested.

ENGINEER’S REPORT – SCOTT RIGHTS

The following is an update on work completed by our office during the past month.

- Wastewater Treatment Plant & Collection System Issues:

a.	Sewer Main Cleaning and Televising:  USG was authorized to proceed on March 16.  A definitive start date has not been established.  The intent is to complete the work during an upcoming wet weather period if possible.  USG will continue to coordinate with NLCA in selecting a time that suits both parties.

b.	Transition to Place Treatment Train #2 on line:  NLCA and our office continued discussions on when to place the second process train in service and what revisions are needed to the facility prior to doing so.  In addition, a meeting has been scheduled for Wednesday August 8 at the treatment plant to discuss options for replacing the existing DelPac feed line and possibly issues revealed during the recent high rains.

2.	2017 Chapter 94 Annual Wasteload Management Report:  PADEP issued correspondence on July 31, 2018 approving the report.

3.	Land Development Projects:  The following is an update on proposed land development projects and reviews as they relate to sanitary sewer.

a.	Lickdale 81-Unit Hotel (Route 72):  This project has been granted conditional final land development plan approval.  All sanitary sewer issues have been addressed including the PADOT Highway Occupancy Permit and the easement agreement across the Lickdale Fire Company property.  (No change since last Board meeting).

b.	Logistics Park, Phase 2 Warehouses (Vision Acquisitions III):  This project is in the construction phase.  Construction of the low-pressure sewer in Bordnersville Rd. was completed last month.  During the past month, the contractor cleared the right of way across Logistics Park Lot #1 in anticipation of commencing the cross-country work and connection to the terminal cleanout manhole just upstream of the existing Logistics Park Pump Station.

c.	70 Bordnersville Rd (Brewsters):  This project is in the construction phase.  During the month, the contractor completed the hydrostatic testing of the low-pressure sewer between the grinder pump station and the edge of Township road right of way.  Work remaining includes making the final connection to the recently installed Logistics Park Phase 2 low pressure sewer in Bordnersville Rd. and testing grinder pump station.

4.	Standard Sanitary Sewer Construction Specifications:  The updated administrative procedures were provided to the Township manager late last week for review and comment.  Upcoming schedule includes meeting with Township Manager on August 16 to review technical specifications and details.

Scott Rights also informed the Board that Love’s currently has 29 EDUs, but their usage is going up again.  He also noted that Liz Krause informed him that she had a phone call that they were interested in putting in more showers which could increase their water usage even more.  Atty. Bametzreider commented that last year he sent a letter to Rick Shuffield of Love’s, advising him that the Township was going to monitor Love’s usage to determine if additional EDUs had to be purchased; and over the course of the past year they have used as high as 14 additional EDUs.  After discussing the matter, Dennis Firestone made a motion seconded by Kerry McCrary to authorize Atty. Bametzreider to send Rick Shuffield of Love’s a letter notifying them, that due to their usage, they are required to purchase 14 additional EDUs. All approved.

Liz Krause explained to the Board that Speedway has, again, used an extreme amount of water, and noted that last quarter she was notified by the City of Lebanon (COLA) that they had a large water leak, and the Board authorized Krause to just bill them at the regular rate as suggested by COLA. Krause noted that she contacted COLA regarding Speedway’s high-water usage; but was not able to confirm if there were any leaks reported for the billing cycle.  After a brief discussion, Dennis Firestone made a motion seconded by Kerry McCrary to authorize Liz Krause to bill Speedway for their total usage unless the City of Lebanon provides a good explanation that there was another leak.  All approved.

SOLICITOR’S REPORT – PAUL BAMETZREIDER -

Atty. Bametzreider said that pending any questions, he had nothing new to report other than what was previously discussed.

BILLS

Dennis Firestone made a motion seconded by Gary Longenecker to pay the bills in the

amount of $20,696.82 from the sewer fund.  All approved.

DATE OF NEXT LICKDALE TREATMENT PLANT MEETING

Wednesday, September 12, 2018 at 6:30 P.M

ADJOURNMENT

The meeting was adjourned at 6:55 p.m.

Respectfully submitted,

Elizabeth Krause

Recording Secretary