November 14, 2018

Lickdale, PA

The Union Township Board of Supervisors held a scheduled sewer meeting on

November 14, 2018.  The meeting was held at the Municipal Building, 3111 SR 72, Jonestown, PA.

Chairman Firestone called the meeting to order at 6:30 PM.

Present:		Dennis Firestone, Chairman

Kerry McCrary, Vice Chairman

Gary Longenecker, Secretary

Paul Bametzreider, Township Solicitor

Scott Rights, Sewer Engineer

Brent McFeaters, Township Manager

Elizabeth Krause, Zoning Officer

Tad Barnhart, Operator

Three (3) Citizens

PUBLIC COMMENTS

APPROVE THE MINUTES

Chairman Firestone presented the minutes from the October meeting for approval.  Kerry McCrary made a motion seconded by Dennis Firestone to approve the October meeting minutes.   All approved.

APPROVE THE FINANCIAL REPORT

Gary Longenecker made a motion seconded by Kerry McCrary to approve the Financial Report.  All approved.

OPERATOR’S REPORT – Tad Barnhart

- Envirep Service Contract – Tad Barnhart said it’s time to renew the Envirep annual preventative maintenance agreement in the amount of $2,850.00 for maintenance on all the pumps at the stations.  Dennis Firestone made a motion seconded by Kerry McCrary to approve renewing the preventative maintenance agreement with Enivep.

- Chemical Tank Leak – Tad reported that the repairs were made with new tank fittings and   to date, everything is good.

- Sampler Platform is Complete – Tad explained that the platform is complete and was built to prevent heavy rain from causing flood damage to the effluent sampler.

- Screen Room – The water line with new filter and dampener is complete.  He noted that the old housing got cracked from pressure surges.

- Impeller Replaced – Tad reported that the impeller was replaced for the main sludge return pump in October and is working fine.

- Pump Station #2 (UGI) Pressure – Tad explained that they were having issues with the gas pressure not being high enough at Pump Station #2.  He said that UGI put in a new pressure meter and the pressure is at the correct level, but the voltage seems to be fluctuating but Penn Power is working with the vendor MTU to correct the problem.

- Carwash Omnisite Meter.  Tad reported that the Liberty Carwash’s Omnisite Meter is not working correctly because it can’t measure how much water is leaving the carwash, and since it isn’t accurate, it shouldn’t be used for billing adjustment purposes.  Liz Krause noted that on the previous sewer billing,  the charge for one EDU was deducted from the Carwash’s sewer bill because she used the readings that were provided by the omnisite meter which showed one less EDU being used than what the City of Lebanon’s readings showed.   She asked if the charge for the usage of the additional EDU should be added to the Car Wash’s November’s billing.  After discussing the matter with Scott Rights, Sewer Engineer and Paul Bametzreider, Township Solicitor, the Board agreed that the charge for one EDU that was deducted from the previous bill, should be added to the car wash’s November sewer bill.

- Pump Station 3 must be updated to 4G – Tad explained that the wireless communication device at Pump Station 3 will have to be updated to 4G by December 2019 because 3G is now being phased out.  Tad said the cost to upgrade will be $300.00 and asked if the Board wanted it taken care of now or if they wanted to wait to do the upgrade.  The Board agreed that the upgrade should be made now so it’s taken care of.

- Lastly Tad informed the Board that Envirep and the NLCA are collaborating to figure out why the Inground raw pump was losing it’s prime and where the air is getting in, because when the pump is running, it’s fine.

ENGINEER’S REPORT – Scott Rights

- Wastewater Treatment Plant & Collection System Issues:

a.	Chemical Feed Yard Piping:  SLH is scheduled to commence work the week of November 19.  A site meeting was held on Tuesday, November 13 with the SLH, NLCA and our office to review the scope of work.

b.	Transition to Place Treatment Train #2 on line:  Miles T. Weaber informed us they are scheduled to complete the stainless steel screen riser, transfer port cover plate and the overflow baffle fabrications towards the end of November.  DESCCO is anticipating starting soon thereafter to mount the fabrications and to complete the other improvements to Train #2 which is currently not being utilized.  The current plan is to place Train #2 on line sometime in spring 2019.  After the biological activity in Train #2 has acclimated, Train #1 shall be drained and temporarily removed from service to allow DESCCO to the complete the same improvements to Train #1.  Once completed, Train #1 shall be returned to service such that both trains shall be operating simultaneously.

c.	Leak in Sodium Hydroxide Piping:  George Strohm completed the initial work of replacing the PVC pump suction and tank drain lines associated with the sodium hydroxide storage tank during the month thus allowing the tank to be returned to service.  Replacing the balance of the PVC, fittings and valves inside the chemical storage room shall be coordinated with the work being completed by SLH.

2.	Land Development Projects:  The following is an update on proposed land development projects and reviews as they relate to sanitary sewer.

a.	Lickdale 81-Unit Hotel (Route 72):  This project has been granted conditional final land development plan approval.  All sanitary sewer issues have been addressed including the PADOT Highway Occupancy Permit and the easement agreement across the Lickdale Fire Company property.  (No change since last Board meeting).

b.	Logistics Park, Phase 2 Warehouses (Vision Acquisitions III):  This project is in the construction phase.  Construction of the low-pressure sewer system has been completed and hydrostatic tested including the segment across Logistics Park Lot #1.

c.	70 Bordnersville Rd (Brewsters):  Construction of the low-pressure sewer system including hydrostatic testing was completed during month.

3.	Standard Sanitary Sewer Construction Specifications:  Our office continues to finalize the technical specification revisions and standard drawing details.

4.	Tier II Report for Chemicals used at the WWTP:  We continue to prepare the Tier II report to register chemicals used at the Lickdale Wastewater Treatment Plant as directed by the Township.  Scott noted that the report is done and they will get it sent in.

SOLICITOR’S REPORT – PAUL BAMETZREIDER -

None

BILLS

Dennis Firestone made a motion seconded by Kerry McCrary to pay the bills in the

amount of $156,567.17 from the Sewer Fund.  All approved.

DATE OF NEXT LICKDALE TREATMENT PLANT MEETING

Wednesday, December 12, 2018 at 6:30 P.M

ADJOURNMENT

The meeting was adjourned at 6:53 p.m.

Respectfully submitted,

Elizabeth Krause

Recording Secretary