November 13, 2019

Lickdale, PA

The Union Township Board of Supervisors held a scheduled sewer meeting on November 13, 2019.  The meeting was held at the Municipal Building, 3111 SR 72, Jonestown, PA.

Chairman Firestone called the meeting to order at 6:30 PM.

Present:		Dennis Firestone, Chairman

Kerry McCrary, Vice Chairman

Gary Longenecker, Secretary

Atty. Andrew Race for Paul Bametzreider, Township Solicitor

Scott Rights, Sewer Engineer

Brent McFeaters, Township Manager

Elizabeth Krause, Zoning Officer

Tad Barnhart, Operator

Three (3) Citizens

PUBLIC COMMENTS

None

APPROVE THE MINUTES

Chairman Firestone presented the minutes from the October meeting for approval.  Gary Longenecker made a motion seconded by Kerry McCrary to approve the October meeting minutes.   All approved.

APPROVE THE FINANCIAL REPORT

Kerry McCrary made a motion seconded by Dennis Firestone to approve the Financial Report.  All approved.

OPERATOR’S REPORT – Tad Barnhart

- Tad Barnhart reported that Hanlen has installed the electric service for the additional lights inside the RAS Vault.

- Tad also informed the Board that they are waiting for the exhaust fan to be delivered so Garden Spot Mechanical can install it inside the RAS Vault.

- Tad said that Jim Darkes has not been able to do the Discharge Report for October because the phone lines have been down.  He added that because the suspended solids are showing to be 10.5 mg. instead of the maximum allowed of 10.0, the Township could receive a Notice of Violation from DEP.  He said that the reason for the increase in the suspended solids is because the red worm larvae are now dying off after being treated and are becoming suspended solids.

ENGINEER’S REPORT – Scott Rights

The following is an update on work completed by our office during the past month.

- Wastewater Treatment Plant & Collection System Issues:

a.	Operator Search:  We continue to assist the Township in their search for a new 	wastewater system operator effective January 1, 2020.  Related to the matter, we 	are working with the Township Solicitor to prepare a Request for Proposal (RFP) 	to fill the position.

b.	Sewer System Budgeting:  Our office continued during the month to assist the 	Township in preparing the 2020 Wastewater System Budget.

2.	Land Development Projects:  The following is an update on proposed land development projects and reviews as they relate to sanitary sewer.

a.	Freightliner of Lebanon (SE corner of SR 0072 and Old Forge Rd):  The Developer submitted revised plans (2nd submission) which we reviewed and provided comments.  The plans are proposing connection to existing sewers in Old Forge Rd. just opposite Love’s Truck Stop.  In addition, the Developer has requested 2 EDUs (500 gpd) of sewer capacity.  As per our November 11 email, we recommend the Township approve the request.  Dennis Firestone made a motion seconded by Gary Longenecker to approve Freightliner’s request for two (2) EDU’s of sewer capacity.  All approved.

b.	Fisher Ave. Hotel:  The Developer submitted revised plans (2nd submission) which we reviewed and provided comments.  The plans are proposing connection to the Township’s low-pressure sewer (LPS) system behind the Pit Stop Carwash.  The LPS system ultimately drains into the Township’s Pump Station #2 located adjacent to Ingram Micro.  Because the Ingram Micro station has capacity limitations, we have requested the Developer make application for capacity so that a capacity evaluation can be made if necessary.  The Developer has yet to make application.

3.	Standard Sanitary Sewer Construction Specifications:  Our office continues to finalize the technical specification revisions and standard drawing details.

SOLICITOR’S REPORT –

Atty. Andrew Race filling in for Paul Bametzreider, Township Solicitor said that he looked over the RFP and it is appropriate to release.  Brent said the addendum was done.

Atty. Race said Paul Bametzreider sent Sam Sharma a letter because of his failure to make payment for his reserve EDUs and Atty. Bametzreider added that Mr. Sharma called a few days ago, but he hasn’t been able to return his call.

NEW BUSINESS – None

OLD BUSINESS – None

None

BILLS

Dennis Firestone made a motion seconded by Gary Longenecker to pay the bills in the

amount of $27,607.76 from the Sewer Fund.  All approved.

DATE OF NEXT LICKDALE TREATMENT PLANT MEETING

Wednesday, December 11, 2019 at 6:30 P.M

ADJOURNMENT

The meeting was adjourned at 6:43 p.m.

Respectfully submitted,

Elizabeth Krause

Recording Secretary