February 12, 2020

Lickdale, PA

The Union Township Board of Supervisors held a scheduled sewer meeting on February 12, 2020.  The meeting was held at the Municipal Building, 3111 SR 72, Jonestown, PA.

Chairman Firestone called the meeting to order at 6:30 PM.

Present:		Dennis Firestone, Chairman

Kerry McCrary, Vice Chairman

Gary Longenecker, Secretary

Paul Bametzreider, Township Solicitor

Scott Rights, Sewer Engineer

Brent McFeaters, Township Manager

Elizabeth Krause, Zoning Officer

Paul Bametzreider, Township Solicitor

Dusty Keller, Operator

Three (3) Citizens

PUBLIC COMMENTS

None

APPROVE THE MINUTES

Chairman Firestone presented the minutes from the January meeting for approval.  Gary Longenecker made a motion seconded by Kerry McCrary to approve the January meeting minutes.   All approved.

APPROVE THE FINANCIAL REPORT

Kerry McCrary made a motion seconded by Gary Longenecker to approve the Financial Report.  All approved.

OPERATOR’S REPORT – Dusty Keller

Dusty Keller reported that there was a toilet valve stuck open at the unoccupied warehouse next to the Ferrero Roche warehouse  and the plant saw some increased flow for a few days, but the problem has been fixed.

He also reported that the clock motor on the chart recorder for the final went bad.  It’s an older unit so there are no parts available anymore.  He said hey purchased a used one from W. G. Malden for $350.00 instead of purchasing a new unit that would have cost between $1,200 to $1,500.00.  Dusty added that the plant is running well.

Kerry McCrary said he was going through the November inspection report and saw that the report stated that the electrical conduit and metal supports around and above the EQ tanks continue to rust from hydrogen sulfide and should be addressed before failure.   Dusty said the conduit used was a carbon steel and it should have been stainless, and the surface is rusting because

there is hydrogen sulfide coming off that tank which is normal. Dusty said at some point in the future it would be good to replace it with plastic conduit or aluminum. Scott Rights added that if at some point the Township has to increase capacity at the plant, that would be a good time to replace it.

EXECUTIVE SESSION

Dennis Firestone announced that the Board held an Executive Session before the meeting to discuss possible litigation issues.

ENGINEER’S REPORT – Scott Rights

The following is an update on work completed by our office during the past month

- Wastewater Treatment Plant & Collection System Issues: There are no issues at either the WWTP or in the collection system that we are aware of.

2.	Land Development Projects:  The following is an update on proposed land development projects and reviews as they relate to sanitary sewer.

a.	Freightliner of Lebanon (SE corner of SR 0072 and Old Forge Rd):  The Developer submitted revised plans (3rd submission) which we reviewed and provided comments.  The plans are proposing connection to existing sewers in Old Forge Rd. just opposite Love’s Truck Stop.

b.	Fisher Ave. Hotel:  The Developer submitted revised plans (3rd submission) which we reviewed and provided comments.  The plans are proposing connection to the Township’s low-pressure sewer (LPS) system behind the Pit Stop Carwash.  In addition, the Developer made application to the Township for 6,000 gpd (24 EDUs) of sewer capacity.  We completed our evaluation to confirm capacity is available at both the WWTP and in the Ingram Micro Pump Station (Township Pump Station #2).

c.	Logistics Park Phase 2:  The Developer has advised us they are interested in 	preparing deed of dedication documents for dedication of the low pressure sewers 		to the Township.  Our office is working with the Township Solicitor to prepare the 	documents and a list of information required from the Developer.

3.	Chapter 94 Annual Wasteload Management Report:  Our office began preparation of the report which is due PADEP by March 31.  The purpose of the report is to determine if the WWTP is overloaded (hydraulically and organically) or is projected to be overloaded within the next five (years).  The computations indicate that the WWTP is neither currently overloaded nor is it projected to be overloaded within the next five (5) years.  The average daily flow for 2019 computed to 84,000 gallons per day (gpd).  The WWTP is permitted for an annual average flow of 150,000 gpd and a maximum monthly of 210,000 gpd.  A draft copy of the PADEP spreadsheet is attached.  A complete draft of the report will be emailed to the Board prior to the Board’s March 11 meeting for review and comment.

4.	Standard Sanitary Sewer Construction Specifications:  Our office continues to finalize the technical specification revisions and standard drawing details.

HOME TWO SUITES SEWER CAPACTIY APPLICATION

Scott Rights said that as he explained earlier in his report, they received an application from the Developer of Home 2 Suites for  6,000 gallons a day of capacity (24 EDUs), and that capacity is available at both the WWTP and the Ingram Micro Pump Station. Scott added that as part of the land development process the developer must do sewage facilities planning.  He explained that they are doing an exemption, that because there are no overloads in the Township’s system, and they don’t need any kind of permitting from DEP to build the sewer system from that particular site, they can do what they call an “exemption”.  The document that needs to be signed as part of that is saying that as owner of the sewer system, the capacity exists in the sewer system.  Scott said that he would recommend that the Board approve the 6,000 gallons a day of capacity plus authorize Brent to sign the Planning Module Exemption.  Dennis Firestone made a motion seconded by Kerry McCrary to approve 6,000 gallons of sewer capacity for Home 2 Suites and authorize Brent McFeaters, Township Manager to sign the Planning Module Exemption.  All approved.

SOLICITOR’S REPORT – PAUL BAMETZREIDER

Atty. Bametzreider said he had nothing new to report but noted that at some point he will have to draw up a sewer capacity agreement for Home Two Suites.

NEW BUSINESS

MOTION TO APPROVE THE PREVENTATIVE MAINTENANCE CONTRACT WITH PENN POWER FOR THE PLANT GENERATOR (2-YEAR TERM CONTRACT)

Brent McFeaters, Township Manager explained that this is a two-year agreement for the generator that is at the sewer treatment plant and Pump Station #2 and the cost is $1,740.00 per year.  Gary Longenecker made a motion seconded by Kerry McCrary to approve the Preventative Maintenance contract with Penn Power for the generator at the sewer treatment plant and Pump Station #2.  All approved.

OLD BUSINESS – None

OTHER COMMENTS - None

BILLS

Dennis Firestone made a motion seconded by Kerry McCrary to pay the bills in the

amount of $28,213.25 from the Sewer Fund.  All approved.

Glenn Rudy asked about the status of Kyle Boltz EDUs and Paul Bametzreider said he is made his 2019 payment for the purchase of the three additional EDUs and he paid his November sewer bill.  He added that he will be due to pay his 2020 payment for three additional EDUs on December 31st.

DATE OF NEXT LICKDALE TREATMENT PLANT MEETING

Wednesday, March 11, 2020 at 6:30 P.M

ADJOURNMENT

The meeting was adjourned at 6:45 p.m.

Respectfully submitted,

Elizabeth Krause

Recording Secretary